## Slide 1: Electrical fires can be prevented!
By PowerCheck

## Slide 2: In This well kept older home…

## Slide 3: A SERIOUS Fire hazard wAS present
Deteriorated live conductors at service entrance of house, millimeters away from flashing and creating fire

## Slide 4: immediate attention was requested
Within one hour homeowner had their electrician on site to prepare new installation of electrical service

## Slide 5: Key Fire Hazards in OLDER HOUSES, DUE to Deterioration
Ground clamp has broken away from copper water pipe, increasing risk of fire and electrocution

## Slide 6: Handyman Add-ons
Multiple circuits hazardously installed, putting house at increased risk of electrical fire

## Slide 7: Handyman alterations
Burnt out pigtails on aluminum wire due to incorrect wire connectors

## Slide 8: Old houses should to be checked thoroughly for Electrical safety

## Slide 9: If it hasn’t been checked since new, it’s high time overdue !

## Slide 10: Problems WITH ELECTRICAL PANELS: Oversized circuit breakers
200 amp circuit breaker
60 amp service
This house is at increased risk of electrical fire

## Slide 11: Obsolete circuit breakers
These circuit breakers, “Square D, Type XO” are no longer installed, as they do not meet modern specifications, putting house at increased risk of fire

## Slide 12: Burnt-out circuit breakers

## Slide 13: Loose electrical connections
As houses age, electrical connections often become loose, increasing risk of electrical fire

## Slide 14: And on occasion: A Complete disregard for safety
Original main fuses, in service switch replaced with short lengths of copper water pipe

## Slide 15: Some repairs compromise the electrical system
Repair of copper pipe with plastic PEX breaks the electrical grounding of the house

## Slide 16: In old Homes Electrical wires are often found live!
Often found in the basement, and sometimes in the vicinity of the gas pipe, live wire creates risk of fire and electrocution.
Live electrical conductor found millimeters from gas pipe

## Slide 17: SOME Tidy-ups done by homeowners create serious fire hazards
Metal staples securing cord, over time can easily cut into the cord, creating fire

## Slide 18: SOME ACTIONS BY occupants set scenario for fire

## Slide 19: IN OLDER HOUSES Fire Hazards are everywhere!
Unfilled knock outs commonly called “Mouse holes” provide easy access to the warmth in an electrical box

## Slide 20: Connections not in boxes
Live electrical connections sandwiched between wooden boards

## Slide 21: In old houses Handyman Add-on circuits are abundant
Installer failed to install an electrical box behind this dryer outlet, putting house at increased risk of fire

## Slide 22: baseboard heater Often found hazardously installed
Installer failed to install a “box connector” to
protect cable, putting house at increased risk of fire

## Slide 23: Cables without protection
Installer failed to install “Anti-short” on this cable to a new furnace, putting house at risk of fire”

## Slide 24: Add-on Light Fixtures
Installer failed to install a junction box behind this add-on lampholder, putting house at increased risk of fire.

## Slide 25: Knob and tube has concerns

## Slide 26: Knob and tube has solutions

## Slide 27: Aluminum Wire Has Concerns

## Slide 28: Aluminum has Solutions: However, Copper Pigtailing MAY increase RISK
Copper Pigtailing on aluminum conductors CANNOT be done with standard wire connectors

## Slide 29: Cables for inDoors are not for outdoors
Old indoor cables have deteriorated, taped with duct tape by occupant. House is now at increased risk of fire.

## Slide 30: HANdyman add-on circuits: Often found with NO regard for safety

## Slide 31: With a thorough electrical Check-up, on a regular basis, Old Houses can remain safe forever
Thank you